## Slide 1: Linear Regression Scenarios(method)
Stage 1:
  Option 1: (Flow2power)
  Option 2: (Tset2power)
  Fan power model and chiller power model training:
    Obtain and ( is known, )
Stage 2:
  Calculate fan power and chiller power:
    where , =
  Calculate temperature prediction (explicit for Option1):
    For Option 2:
Stage 3:
  1min vs 60 min interval

## Slide 2: Linear Regression Scenarios(Tset2power)
VB air mass flow dynamics
  , for t=1
  , for t=2,3,…,K
  Where is the initial zone temperature, are the zone cooling setpoints temperatures.(t=1,2,…,K)
Fan power model and chiller power model training:
  Calculate fan power and chiller power:
    where , =
Objective:
  Minimize

## Slide 3: Linear Regression Results
  Currently missing data:
    Room# 002 004 100 121 missing lighting power
 | Opt1(flow2power) |  | Opt2 (Tset2power) | 
 | 1min | 60min | 1min | 60min
RMSE for Mass flow rate(%) | 0 | 0 | 13.55% | 11.59%
Mean RMSE for the temperature prediction (K) start from 0am | 3.54 | 1.86 | 1.49e-15 | 2.13e-15
Max RMSE for occ period(8am~5pm) | 2.66 | 2.09 |  | 
Option 2 gives smaller prediction error generally and 1 min
->3.66 when start from 12pm, no significant change

## Slide 4: Zone flow Regression Results
2 weeks
Chart: Tzone102
Chart: Zone 104
2 weeks

## Slide 5: Zone flow Regression Results
2 weeks
2 weeks
Chart: Zone 105
Chart: Zone 107

## Slide 6: Zone flow Regression Results
2 weeks
2 weeks
Chart: Zone 108
Chart: Zone 112

## Slide 7: Zone flow Regression Results
2 weeks
2 weeks
Chart: Zone 116
Chart: Zone 118

## Slide 8: Zone flow Regression Results
2 weeks
2 weeks
Chart: Zone 119
Chart: Zone 120

## Slide 9: Zone flow Regression Results
2 weeks
2 weeks
Chart: Zone 123A
Chart: Zone 123B

## Slide 10: Zone flow Regression Results
2 weeks
2 weeks
Chart: Zone 127A
Chart: Zone 127B

## Slide 11: Zone flow Regression Results
2 weeks
2 weeks
Chart: Zone 129
Chart: Zone 131

## Slide 12: Zone flow Regression Results
2 weeks
2 weeks
Chart: Zone 133
Chart: Zone 136

## Slide 13: Zone flow Regression Results
2 weeks
2 weeks
Chart: Zone 142
Chart: Zone 143

## Slide 14: Zone flow Regression Results
2 weeks
2 weeks
Chart: Zone 150
Chart: Zone CORRIDOR

## Slide 15: Zone flow Regression Results
2 weeks
Chart: Zone RESTROOM

## Slide 16: Zone Supply Temperature Regression Results
2 weeks
2 weeks
Chart: AHU-002
Chart: AHU-004

## Slide 17: AHU Fan Power Regression Results
2 weeks
2 weeks
Chart: AHU-001
Chart: AHU-002

## Slide 18: AHU Fan Power Regression Results
2 weeks
2 weeks
Chart: AHU-003
Chart: AHU-004

## Slide 19: Chiller Power Regression Results
2 weeks
Chart: 

## Slide 20: 24 Hour result analysis
Possible issue existing in the plot
  1 hour delay between Tset and Tpred
  Tpred is MPC solution from 1am to 24pm, while Tset is implemented in eplus from 1am to 24pm, but actually there are 1 hour delay in Tset.
  The peak in Tpred is sort of matching with price peak.

## Slide 21: 24 Hour result analysis
Possible issue existing in the plot
  Relaxation too high
  This can be reduced by using larger penalty term parameters, while the optimality of solution could be compromised
  Is there better way to solve it?

## Slide 22: 24 Hour result analysis
Possible issue existing in the plot
  The Tset is oscillating instead of showing peak and bottom
  In the right plot, the temperature reached the upper bound early and can’t give higher Tset at the peak, which can explain why the oscillation almost flat

## Slide 23: The other work undergoing
New dockerfile for Julia engine with optimized IPOPT installation
  Meeting issues with license installation

## Slide 24: VB+TES+ES
Power transfer limits constraint
binary
Charging/discharging mode constraint
SOC dynamics =
SOC level limits
Chiller water temperature constraint
Initial and Terminal condition for SOC
Power transfer limits constraint
binary
Charging/discharging mode constraint
SOC dynamics =
SOC level limits
Initial and Terminal condition for SOC
Cycle limit(optional)
Building Thermal Dynamics (VB)
TES
ES (BTM only)
Total Building Cooling Load
Thermal comfort constraints
Power limit constraints
Minimize
Electric Power balance
Thermal Power balance
Notes: Uncontrollable Power

## Slide 25: VB+TES+ES
Power transfer limits constraint
Charging/discharging mode constraint
Chiller water temperature constraint
SOC dynamics
SOC level limits
Initial and Terminal condition for SOC
Power transfer limits constraint
Charging/discharging mode constraint
SOC dynamics
SOC level limits
Initial and Terminal condition for SOC
Number of Cycle limit
Virtual Battery
TES
ES(BTM only)
Total Building Cooling Load
Thermal comfort constraints
Power limit constraints
Minimize
Electrical Power Balance
Thermal Power Balance

## Slide 26: VB+TES+ES
o
Discharging Process
Discharging Process
Cool Capacity
Demand
Grid
Charging Process
Charging Process
Chiller 1
Charge
Discharge
ES
TES
Discharging power
Charging power
Chiller power 2
IS charging rate
IS discharging rate
Charge
Discharge
Uncontrollable Load (heat)
Chiller Cooling rate 1
=
Chiller 2
Chiller power 1
Electric power
Cooling power

## Slide 27: VB+TES+ES zero balance
Thermal power
Electric power
Virtual Battery
TES chiller(chiller 2)
Base load chiller(chiller 1)
ES
Grid
Purchase power
Chiller power
+

## Slide 28
Mode | TESS | Chiller
 | Storage | Chiller
1 | Disabled | Cooling
2 | Cooling | Disabled
3 | Cooling | Cooling
4 | Cooling | Charging
5 | Cooling | Cooling + Charging
Missing 3 cases:
all disabled
Storage disabled, charging+ chiller disabled
Storage disabled, cooling + charging?