## Slide 1: Linear Regression Scenarios(method)
Stage 1:
  Option 1: (Flow2power)
  Option 2: (Tset2power)
  Fan power model and chiller power model training:
    Obtain and ( is known, )
Stage 2:
  Calculate fan power and chiller power:
    where , =
  Calculate temperature prediction (explicit for Option1):
    For Option 2:
Stage 3:
  1min vs 60 min interval

## Slide 2: Linear Regression Results
  Currently missing data:
    Room# 002 004 100 121 missing lighting power
 | Opt1(flow2power) |  | Opt2 (Tset2power) | 
 | 1min | 60min | 1min | 60min
RMSE for Mass flow rate(%) | 0 | 0 | 13.72% | 18.14%
Mean RMSE for the temperature prediction (K) start from 0am | 3.54 | 1.86 | 1.49e-15 | 2.13e-15
Max RMSE for occ period(8am~5pm) | 2.66 | 2.09 |  | 
Option 2 gives smaller prediction error generally and 1 min
->3.66 when start from 12pm, no significant change

## Slide 3: Linear Regression Results
24 hours
24 hours

## Slide 4: VB+TES+ES
Power transfer limits constraint
binary
Charging/discharging mode constraint
SOC dynamics =
SOC level limits
Chiller water temperature constraint
Initial and Terminal condition for SOC
Power transfer limits constraint
binary
Charging/discharging mode constraint
SOC dynamics =
SOC level limits
Initial and Terminal condition for SOC
Cycle limit(optional)
Building Thermal Dynamics (VB)
TES
ES (BTM only)
Total Building Cooling Load
Thermal comfort constraints
Power limit constraints
Minimize
Electric Power balance
Thermal Power balance
Notes: Uncontrollable Power

## Slide 5: VB+TES+ES
Power transfer limits constraint
Charging/discharging mode constraint
Chiller water temperature constraint
SOC dynamics
SOC level limits
Initial and Terminal condition for SOC
Power transfer limits constraint
Charging/discharging mode constraint
SOC dynamics
SOC level limits
Initial and Terminal condition for SOC
Number of Cycle limit
Virtual Battery
TES
ES(BTM only)
Total Building Cooling Load
Thermal comfort constraints
Power limit constraints
Minimize
Electrical Power Balance
Thermal Power Balance

## Slide 6: VB+TES+ES
o
Discharging Process
Discharging Process
Cool Capacity
Demand
Grid
Charging Process
Charging Process
Chiller 1
Charge
Discharge
ES
TES
Discharging power
Charging power
Chiller power 2
IS charging rate
IS discharging rate
Charge
Discharge
Uncontrollable Load (heat)
Chiller Cooling rate 1
=
Chiller 2
Chiller power 1
Electric power
Cooling power

## Slide 7: VB+TES+ES zero balance
Thermal power
Electric power
Virtual Battery
TES chiller(chiller 2)
Base load chiller(chiller 1)
ES
Grid
Purchase power
Chiller power
+

## Slide 8
Mode | TESS | Chiller
 | Storage | Chiller
1 | Disabled | Cooling
2 | Cooling | Disabled
3 | Cooling | Cooling
4 | Cooling | Charging
5 | Cooling | Cooling + Charging
Missing 3 cases:
all disabled
Storage disabled, charging+ chiller disabled
Storage disabled, cooling + charging?